Notification of the Failure to Meet the Parametric Values in Part 1 of the Schedule of the European Communities (Drinking Water)(No. 2) Regulations, 2007 (S.I. No 278 of 2007) in Accordance with Regulation 9(1) or 10(2)

| Local authority | Galway County Council |
| --- | --- |
| Name of Water Supply Zone | Kinvara P.S |
| Water Supply Zone Code | 1200PUB1034 |
| Estimated Population Affected | 605 |
| Parameter | THM |
| Result | 147 ug/l |
| Date and Location of Failure | 24th January 2012 @ Fallons Costcutters |
| Notification under Regulation (please tick) | 9(1) |
|  | 10(2) √ |
| Have the Health Service Executive been consulted? | Notification has been issued to the HSE and we are currently awaiting advice. |
| What advice has been provided by the Health Service Executive | See above. |
| Likely Cause and Duration of Failure | In the past treatment on the supply consisted of chlorination only. As stated previously, the caretaker has confirmed that, in order to obtain adequate residuals at the end of the line, it was necessary to dose chlorine at a level that poses a risk of THM formation. This sampling location is fed from a cast iron main which is difficult to flush adequately. It was concluded that the scheme required significant upgrade works and it was included on the RAL. Works are complete on the installation of coagulation, filtration and UV treatment. The contractors were waiting for sufficient water to be available to commissioning of the plant and this is now scheduled for completion in March. It is expected that the new treatment works will address the THM issue; however, if this is not the case further investigation will be carried out. |
| Has this parameter exceeded the Parametric Value in this Supply in the past 12 months (if so give details)? | Yes, 5th December 2011 – 201 ug/l at Fallons Costcutters |
| Immediate Action Taken to Inform/Protect Consumers | No immediate action taken. |
| Immediate Corrective Action Taken | The Area Office and Network Management Team were informed. They have recently carried out uni-direcational flushing of the area in which the sample was taken. As stated above the supply is part of the RAL programme and the works are due to be commissioned by March 2012. |

Notified by:			Christina Ryan

Date:				09/02/12

Contact Phone Number:	(091) 476402