Notification of the Failure to Meet the Parametric Values in Part 1 of the Schedule of the European Communities (Drinking Water)(No. 2) Regulations, 2007 (S.I. No 278 of 2007) in Accordance with Regulation 9(1) or 10(2)

| Local authority | Galway County Council |
| --- | --- |
| Name of Water Supply Zone | Inis Oirr PWS |
| Water Supply Zone Code | 1200PUB1025 |
| Estimated Population Affected | 250 year round, increases during summer months |
| Parameter | THM |
| Result | 175 ug/l |
| Date and Location of Failure | 1st August 2012 @ Ostan Inis Oirr |
| Notification under Regulation (please tick) | 9(1) |
|  | 10(2) √ |
| Have the Health Service Executive been consulted? Provide name & contact details. |  |
| What advice has been provided by the Health Service Executive |  |
| Likely Cause and Duration of Failure | During the review by consultants for the Remedial Action List, the Inis Oirr PWS was identified as being at risk for THM exceedances. In order to reduce the THM and other risks it was concluded that the scheme required significant upgrade works and it was included on the Remedial Action List. Works have been completed with the installation of ozone treatment, filtration and UV treatment. The ozone part of the treatment has been switched off due to concerns in relation to the risk of bromate formation. The consultants / contractors are currently preparing a proposal to address this issue as it now their opinion, based on additional raw water data, that ozone is not a suitable treatment process for the raw water on the island. It is understood that they will recommend the installation of a reverse osmosis (RO) system. It is the opinion of the council that the consultant / contractor should have been aware of the risk of bromide in the raw water on occasion due to the evidence of saline intrusion, however, the consultants are arguing that they would not have been aware of this based on the raw water results provided to them. The breakdown of the THM result indicates that bromide in the raw water may be a contributory factor to the non-compliance as bromide has been found to facilitate the formation of brominated trihalomethanes. Bromoform=13.5; Bromodichloromethane=56.8; Chloroform=43.7; Dibromochloromethane=61.1. Galway County Council is in the process of arranging for monitoring of the parameter Total Organic Carbon (TOC) at the plant and in the distribution line as part of the routine monitoring programme for supplies which are at risk for THM formation. As TOC is a good indicator of the likelihood of THM formation it is expected that this will assist in identifying the main source of the pre-cursors. |
| Has this parameter exceeded the Parametric Value in this Supply in the past 12 months (if so give details)? | Yes 109 ug/l on the 29th August 2011 250ug/l on the 23rd August 2011 |
| Immediate Action Taken to Inform/Protect Consumers | All results are provided on our website with information in relation to the various parameters. It is not considered necessary to issue a public notice at this time as it is not considered necessary to restrict the supply. |
| Immediate Corrective Action Taken | As outlined above. |

Notified by:			Christina Ryan

Date:				15/08/12

Contact Phone Number:	(091) 476493