| Local authority | Galway County Council |
| --- | --- |
| Water Supply Zone | Williamstown PWS |
| Water Supply Zone Code | 1200PUB1049 |
| Estimated Population Affected | 180 |
| Parameter | THM |
| Result, Date and Location of Failure | 208ug/l on the 13/06/12 at Texaco (chlorine residual 0.58 mg/l) 208ug/l on the 18/06/12 at Texaco (chlorine residual 0.23 mg/l) 111ug/l on the 27/06/12 at Texaco (chlorine residual 0.72 mg/l) |
| Notification under Regulation (please tick) | 9(1) |
|  | 10(2) √ |
| Have the Health Service Executive been consulted? Provide name & contact details. | Yes Gerry Leen, Senior EHO |
| What advice has been provided by the Health Service Executive | The HSE requested confirmation of the dates for completion of the proposed additional uni-directional flushing and the proposed review of the results using the SCADA system which is in the process of installation in Galway County Council. In relation to all of the non-compliances the HSE recommended monitoring to determine the pattern and presence of the THM in the supply. We are in the process of obtaining quotations for including TOC monitoring at the plant and on the line as part of the check and / or audit monitoring for supplies which are at risk for THM formation and the HSE have agreed that this will comply with their recommendation. |
| Likely Cause and Duration of Failure | Works have been completed on the installation of ozone treatment, activated carbon filter and UV treatment and Galway County Council are now running the plant. Spikes in colour have caused issues with the ozone treatment system on occasion. A SCADA system is currently being provided for the Divisional Team and they propose to carry out a review of results to determine whether the THM issue is from the plant or the network or a combination of both. The initial phase of a programme of uni-directional flushing was completed in Jan-Mar 2012 and further flushing is proposed. |
| Has this parameter exceeded the Parametric Value in this Supply in the past 12 months | 121 ug/l - 21st October 2011 @ Mace Shop, Williamstown |
| Immediate Action Taken to Inform/Protect Consumers | The HSE has not made any recommendation to notify the public. Results will be posted on website as per normal procedure. |
| Immediate Corrective Action Taken | See above. |

Notified by:			Christina Ryan, Assistant Scientist

Date:				16/07/12

Contact Phone Number:	(091) 476402