Notification of the Failure to Meet the Parametric Values in Part 1 of the Schedule of the European Communities (Drinking Water)(No. 2) Regulations, 2007 (S.I. No 278 of 2007) in Accordance with Regulation 9(1) or 10(2)

| Local authority | Galway County Council |
| --- | --- |
| Name of Water Supply Zone | Kinvara P.S |
| Water Supply Zone Code | 1200PUB1034 |
| Estimated Population Affected | 605 |
| Parameter | THM |
| Result, Date and Location of Failure | 214 ug/l at County Council offices on the 12th June 2012 (chlorine residual 0.31mg/l) 192 ug/l at Fallons Costcutter on the 12th June 2012 (chlorine residual 0.64mg/l) A further sample taken on the 26th June at the County Council Offices was compliant (64 ug/l with a chlorine residual of 1.12 mg/l). |
| Notification under Regulation (please tick) | 9(1) |
|  | 10(2) √ |
| Have the Health Service Executive been consulted? | Yes Gerry Leen, Senior EHO |
| What advice has been provided by the Health Service Executive | The HSE have recommended that the contractors, who have been requested to assess the cause of the non-compliance, should be requested to submit their report to the Co. Council before end of July. They also recommend that necessary further actions should be determined following examination of the report. In relation to all of the non-compliances the HSE recommended monitoring to determine the pattern and presence of the THM in the supply. We are in the process of obtaining quotations for including TOC monitoring at the plant and on the line as part of the check and / or audit monitoring for supplies which are at risk for THM formation and the HSE have agreed that this will comply with their recommendation. |
| Likely Cause and Duration of Failure | Works are complete on the installation of a new treatment system including coagulation, filtration and UV treatment. The contractors, who are required to run the plant for the next year, have been requested to assess whether the treatment system was adequately dealing with THM pre-cursors. Fallons Costcutters is fed from cast iron mains which are difficult to flush adequately. This length of pipeline is due for replacement by mid August. |
| Has this parameter exceeded the Parametric Value in this Supply in the past 12 months (if so give details)? | Yes, 5th December 2011 – 201 ug/l at Fallons Costcutters 24th January 2012 - 147 ug/l at Fallons Costcutters |
| Immediate Action Taken to Inform/Protect Consumers | The HSE has not made any recommendation to notify the public. Results will be posted on website as per normal procedure. |
| Immediate Corrective Action Taken | Flushing of the lines have been carried out since the date of the non-compliance. |

Notified by:			Christina Ryan

Date:				09/02/12

Contact Phone Number:	(091) 476402