Appendix A

Notification of the Failure to Meet the Parametric Values in Part 1 of the Schedule of the European Communities (Drinking Water)(No. 2) Regulations, 2007 (S.I. No 278 of 2007) in Accordance with Regulation 9(1) or 10(2)

| Local authority | Galway County Council |
| --- | --- |
| Name of Water Supply Zone | Leenane PWS |
| Water Supply Zone Code | 1200PUB1035 |
| Estimated Population Affected | 100 |
| Parameter | THMs |
| Result, Date and Location of Failure | 181µg/l – 11/06/12, Leenane Community Centre (chlorine residual 0.25 mg/l) 158ug/l – 11/06/12, Leenane Community Centre 166ug/l – 18/06/12, Hamiltons Bar (chlorine residual 0.1 mg/l) 185 ug/l - 25/06/12, Leenane Community Centre (chlorine residual 0. mg/l) |
| /Notification under Regulation (please tick) | 9(1) |
|  | 10(2) √ |
| Have the Health Service Executive been consulted? | Yes Gerry Leen, Senior EHO |
| What advice has been provided by the Health Service Executive | The HSE concur with our proposals as set out below. In relation to all of the non-compliances the HSE recommended monitoring to determine the pattern and presence of the THM in the supply. We are in the process of obtaining quotations for including TOC monitoring at the plant and on the line as part of the check and / or audit monitoring for supplies which are at risk for THM formation and the HSE have agreed that this will comply with their recommendation. |
| Likely Cause and Duration of Failure | Construction of the new treatment plant in Leenane has been completed and commissioning is ongoing. The following treatment has been provided: pre-chlorination, pressure sand filter (Culligan); UV and chlorination with sodium hypochlorite. The raw water is fed from a mountain stream and is subject to spikes in colour and turbidity. The Culligan filter is unable to adequately treat the raw water in the event of a significant increase in colour and turbidity. The contractors have stated that the monitoring available at design stage did not indicate the severity of the spikes that occur on occasion. In response to this issue Galway County Council have installed colour and turbidity monitors on the raw and treated water. A rain gauge has also been installed. It is proposed to assess the data from the gauge and monitors to determine whether there is a correlation between rainfall events and increases in turbidity and colour. If this is the case and the duration of the spike is less than two days, it will be possible to shut down the pumps following significant rainfall events. There is sufficient storage available in Leenane to deal with a spike of less than two days. If, following assessment, it is determined that this option is not feasible it will be necessary to consider providing additional / alternative treatment. |
| Has this parameter exceeded the Parametric Value in this Supply in the past 12 months? | No |
| Immediate Action Taken to Inform/Protect Consumers | The HSE has not made any recommendation to notify the public. Results will be posted on website as per normal procedure. |
| Immediate Corrective Action Taken | As set out above. |

Notified by: 			Christina Ryan

Date:				16/07/12

Contact Phone Number:	(091) 476402