Notification of the Failure to Meet the Parametric Values in Part 1 of the Schedule of the European Communities (Drinking Water)(No. 2) Regulations, 2007 (S.I. No 278 of 2007) in Accordance with Regulation 9(1) or 10(2)

| Local authority | Galway County Council |
| --- | --- |
| Name of Water Supply Zone | Tully/Tullycross Public Water Supply |
| Water Supply Zone Code | GY048 |
| Population Affected | 325 |
| Parameter | THM’s |
| Result, Date and Location of Failure | 118 ug/l on the 01/02/12 at Gala Stores 199 ug/l on the 10/02/12 at Diamonds 57 ug/l on the 17/02/12 at Gala Stores |
| Notification under Regulation (please tick) | 9(1) |
|  | 10(2) √ |
| Have the Health Service Executive been consulted? Provide name & contact details. | Seamus Mitchell, SEHO, HSE West was consulted. |
| What advice has been provided by the Health Service Executive | The HSE have agreed that the actions we propose, as set out below, are satisfactory. They also requested that cleaning of reservoirs be included in the ongoing maintenance programme. |
| Likely Cause and Duration of Failure | Samples were taken as part of the sampling programme for removal of supplies from the RAL list, however, in error the first two samples on this scheme were taken prior to the new plant coming on line on the scheme. The new plant was brought on-line on the 14th February and is currently being commissioned. The scheme was identified as being at risk for THM exceedances due to the nature of the surface water source and the level of treatment in place at the time of the review. It was concluded that the scheme required significant upgrade works and it was included on the RAL. Works are complete on the installation of coagulation, flocculation, DAFF plant, UV and chlorination. Uni-directional flushing and further THM sampling will be carried out on completion of commissioning. |
| Has this parameter exceeded the Parametric Value in this Supply in the past 12 months (if so give details)? | Yes 124 ug/l at the Maol Reidh Hotel on the 02/06/11 |
| Immediate Action Taken to Inform/Protect Consumers | N/A as the new treatment plant has now come on-line. |
| Immediate Corrective Action Taken | N/A as the new treatment plant has now come on-line. |

Notified by: 			Christina Ryan

Date:				29/03/12

Contact Phone Number:	(091) 476402